## Hydraulic
| UNIVERSITY OF SOUTH FLORIDA | Project No: |  |  |  | SC Date: |  |  |  |  | Elevator No:
| Edition: November 1, 2016 | Project Name:
Warranty Phase Elevator Preventative Maintenance
| Hydraulic Elevators |  |  | Initial 12 months basic building warranty phase | [11 empty] | Additional months (if required)
| On Every Visit Complete the Following | Frequency |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6
1 | Inspect & clean machine room, pit, car top, under car, cab & hatch door's sills. | 4 weeks | √
2 | Ride car, checking for unusual noises or operation, make necessary adjustments and/or repairs. Check leveling accuracy on all landings. | 4 weeks | √
Machines
1 | Check & maintain oil· in tank at proper level. Record & report any addition of oil to tanks & file report with Univ. Rep. to account for lost oil. | 4 weeks
2 | Check for leaks around valves & pump making necessary repairs | 4 weeks
3 | Check wear & tension of belt(s), replace & adjust tension as needed. | 4 weeks
4 | Check motor bearings. | 12 weeks
5 | *Motor bearings - lubricate per motor manufacturer's recommendations | 52 weeks
6 | Filter hydraulic fluid & clean reservoir. | 52 weeks
Controller & Relay Panels
1 | Check relays, contractors & selectors, adjust for proper operation, clean contacts, & replace worn or damaged shunts. | 4 weeks
2 | Check for & remove all temporary jumpers. | 4 weeks
3 | Clean controllers. | 12 weeks
4 | Check main line & control fuses for proper ratings, replace if necessary. Turn fuses where ampere rating can be read at all times | 26 weeks
5 | Check voltage to controller & motor connections. | 26 weeks
6 | Timers. | 26 weeks
7 | Check settings & operations of overloads. | 26 weeks
Car
1 | Check alarm bell & 2-way communication. | 4 weeks
2 | Check emergency stop switch operation. | 4 weeks
3 | Check photo cells, infrared safety curtain & safety edge & retraction, clean & adjust as needed. | 4 weeks
4 | Check door speeds & door pressure, check for smooth opening & closing. Adjust as needed. | 4 weeks
5 | *Lubricate car fan or blower, check operation & clean fan grille in cab. | 4 weeks
6 | Check car & hall signal fixtures, including buttons, indicating lights, lanterns & gongs. Replace as needed. | 4 weeks
7 | Clean car station & hall push button contacts. | 12 weeks
8 | Check emergency light operation. | 12 weeks
9 | *Lubricate safety edge linkage pins & adjust. | 12 weeks
10 | Inspect leveling & limit switches. | 12 weeks
Doors - Car Top
1 | Check operation of car top inspection station. | 4 weeks
2 | Check operator's belt(s), bearings, linkage & electric contracts. Replace & adjust as needed. | 4 weeks
3 | Inspect & clean gate switch. | 4 weeks
4 | Check & clean car & hall door tracks, hangers & relating devices. | 4 weeks
5 | Check, adjust & replace as needed door interlocks, pickup rollers & door closures. | 4 weeks
6 | Check car & hall door gibs for wear, replace as needed with proper gibs. | 4 weeks
7 | Inspection car door tracks, hangers, upthrust adjustment & relating devices. | 12 weeks
Pit
1 | Inspect oil lines, buffers, travel cable loop. | 4 weeks
2 | Check for excessive leaking around jack packing. Replace packing when leaking is in excess of three (3) gallons per month. Empty pit can. | 4 weeks
3 | Check the bolster plate & channels. | 26 weeks
Hoistway
1 | Check the stiles for cracks, bends, rust & loose bolts. | 4 weeks
2 | Check adjustment of car shoes and/or roller guides. Replace as needed. | 4 weeks
3 | Check for wear on traveling cable. | 4 weeks
4 | *Lubricate (if required) guide rails, check clips, bolts & brackets. *Fill all lubricators. | 4 weeks
5 | Inspect leveling & limit switches (contact, cam alignment) . Adjust as needed. | 12 weeks
6 | Clean down hoistway. | 52 weeks
Miscellaneous
1 | Check operation of sump pump. Notify Univ. Rep. and/or Service Center if pump does not work properly. (if installed) | Monthly
2 | Check fireman's service operation. | Monthly
3 | Annual relief pressure test. | 52 weeks
| Signature of Mechanic | Date | Required
*Lubricate ltems as required, following manufacturer's recommendation using correct type of lubricant.
PMG-21B

## Traction
| UNIVERSITY OF SOUTH FLORIDA | Project No: |  |  |  | SC Date: |  |  |  |  | Elevator No:
| Edition: November 1, 2016 | Project Name:
Warranty Phase Elevator Preventative Maintenance
| Traction Elevators |  |  | Initial 12 months basic building warranty phase | [11 empty] | Additional months (if required)
| On Every Visit Complete the Following | Frequency |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6
1 | Inspect & clean machine room, pit, car top, under car, cab & hatch door's sills. | 4 weeks | √
2 | Ride car, checking for unusual noises or operation, make necessary adjustments and/or repairs. Check leveling accuracy on all landings. | 4 weeks | √
Machines
1 | Check & inspect machine, motor, motor/generator and governor. | 4 weeks
2 | Check for proper brake operation & clearances, inspect brake lining. | 4 weeks
3 | Check commutators & brushes | 8 weeks
4 | *Lubricate governor linkage. | 12 weeks
5 | Check gear oil level in machine, check machine & motor bearings, end thrust & backlash. | 12 weeks
6 | Blowout motor & motor generator. | 12 weeks
7 | Check motor bearings, coupling & brake operation. | 12 weeks
8 | Check armature clearance & brake cores. | 26 weeks
9 | *Lubricate motor, M/G set, machine bearings, deflector sheaves & governor sheaves. | 52 weeks
10 | *Drop brake shoes & clean, lubricate & adjust. | 52 weeks
11 | Drain, flush & replace gear oil in machine. | 52 weeks
Controllers & Relay Panels
1 | Check relays, contactors & selectors, adjust for proper operation, clean contacts & replace worn or damaged shunts. | 4 weeks
2 | Check for and remove all temporary jumpers. | 4 weeks
3 | Clean controller & selector contacts & relays. | 8 weeks
4 | Check main line & control fuses for proper ratings, replace if necessary. Turn fuses where ampere rating can be read at all times. | 26 weeks
5 | Check voltage to controller & Motor connections. | 26 weeks
6 | Check all resistance tubes, transformers & timers. | 26 weeks
7 | Check settings & operating of overloads. | 26 weeks
8 | Adjust motor control & check logic operation. | 52 weeks
Car
1 | Check alarm bell & 2-way communication. | 4 weeks
2 | Check emergency stop switch operation. | 4 weeks
3 | Safety edge & retraction, clean & adjust for smooth opening & closing. Adjust as needed. | 4 weeks
4 | *Lubricate car fan or blower, check operation & clean fan grille in cab. | 4 weeks
5 | Check car & hall signal fixtures, including buttons, indicating lights, lanterns & gongs. Replace as needed. | 8 weeks
6 | Clean car station & hall push button contacts. | 12 weeks
7 | Check emergency light operation. | 12 weeks
8 | *Lubricate safety edge linkage pins & adjust as needed. | 12 weeks
Doors - Car Top
1 | Check operation of car top inspection station. | 4 weeks
2 | Check operator's belt(s), bearings, linkage & electric contacts, replace & adjust as needed. | 4 weeks
3 | Inspect & clean gate switch. | 4 weeks
4 | Check & clean car & hall door tracks, hangers & relating devices. | 4 weeks
5 | Check, adjust & replace as needed door interlocks, pickup rollers & door closures. | 4 weeks
6 | Check car & Hall door gibs for wear & replace as needed with proper gibs. | 4 weeks
7 | Inspect car door tracks, hangers, upthrust adjustment & relating devices . | 12 weeks
Pit
1 | Inspect safety plant, car & counterweight buffers, governor tail sheave, travel cable loop. | 4 weeks
2 | Inspect car safety mechanism. | 26 weeks
3 | Check oil buffer oil level. | 52 weeks
Hoistway
1 | Check stiles for cracks bends, rust & loose bolts. | 4 weeks
2 | Check adjustment of car shoes and/or roller guides. Replace as needed. | 4 weeks
3 | Check for wear on traveling cable. | 4 weeks
4 | *Lubricate (if required) guide rails, check clips, bolts & brackets. *Fill as lubricators. | 4 weeks
5 | Inspect rope shackles. | 12 weeks
6 | Inspect governor & hoist ropes. Equalize hoist rope tension & check governor rope hitch. *Lubricate hoist ropes as required. | 26 weeks
7 | Clean down hoistway. | 52 weeks
Miscellaneous
1 | Check operation of sump pump. Notify Univ. Rep. and/or Service Center if pump does not work properly. (If installed. ) | Monthly
2 | Check fireman's service operation. | Monthly
3 | Annual no-load safety test. | 52 weeks
| Signature of Mechanic | Date | Required
*Lubricate items as required, following manufacturer's recommendation using correct type of lubrication.
PMG-21B